THE UNIVERSITY OF IOWA

DESIGN STANDARDS & PROCEDURES

September 2023 EDITION

PREFERMENT 02

UIHC Outlets

EFFECTIVE DATE:  October 27, 2023

The information contained in this Preferment modifies, supplements, or replaces information contained in The University of Iowa Design Standards & Procedures.

APPLICABLE SECTION:	Section III – General Design Standards and Outline Specifications and Details

ATTACHMENT(S):	NONE

APPLICABLE TO SECTION III – General Design Standards and Outline Specifications and Details:

ITEM #1	Subsection 26) Electrical

Article 7. Low-Voltage Electrical Distribution

ADD the following article

7.2.13.5.1.4	Require the following for nurse station areas, waiting rooms, and at least one in each inpatient room: NEMA 5-20R Plug Tail Receptacle with USB Charger. 125-volt, 20-amp, hospital grade tamper resistant, 3 wire grounding type with impact resistant thermoplastic face.  USB charging rated 5VDC 2.1A with (1) Type-A port and (1) Type-C port. Mounted in a double gang backbox. Device shall be compatible with all major cell hone and device manufacturers.

END OF PREFERMENT